## Slide 1
OT INFECTION
MONITORING SYSTEM
Real-time Environmental Monitoring for Operating Theatres
Raspberry Pi 4 · SCD30 · BME280 · PMS5003
CO₂
Temperature
Humidity
PM2.5/PM10
Pressure
Compliant: NABH · ASHRAE 170 · WHO IEQ · ISO 14644-1
Intelligent Healthcare · Operating Theatre Safety

## Slide 2
Why Monitor the OT Environment?
Surgical site infections (SSI) are directly linked to uncontrolled environmental parameters
🦠 Surgical Site Infections (SSI)
3–15% of OT procedures result in SSI. Contaminated air is a leading cause. WHO estimates SSIs add 10 extra days to hospital stay.
🌡️ Temperature & Humidity Drift
ASHRAE 170 mandates 20–24°C and 40–60% RH. Violations degrade sterility and affect staff performance and patient thermoregulation.
💨 Particulate Matter (PM2.5 / PM10)
Surgical smoke, skin shedding, and HVAC failure spike PM levels. ISO 14644-1 Class 7 requires <352,000 particles ≥0.5µm per m³.
🌿 CO₂ Accumulation
NIOSH action level: 1000 ppm. Elevated CO₂ indicates insufficient ventilation — raising infection risk and impairing surgeon alertness.

## Slide 3
System Architecture Overview
Three-layer design: Physical sensors → FastAPI backend → Web dashboard
HARDWARE LAYER
▸ SCD30 — CO₂ + Temp + Humidity
▸ BME280 — Barometric Pressure
▸ PMS5003 — PM1 / PM2.5 / PM10
▸ Raspberry Pi 4 (host)
▸ I²C @ 10kHz + UART2 @ 9600
BACKEND LAYER
▸ FastAPI + Uvicorn (port 8001)
▸ HardwareSource (asyncio + threads)
▸ AlarmEngine (hysteresis rules)
▸ SQLite storage (90-day retention)
▸ REST API + WebSocket
▸ HMAC-SHA256 session auth
DASHBOARD LAYER
▸ Single-page HTML/CSS/JS app
▸ Served from backend (same-origin)
▸ Monitor · Alarms · History · Settings
▸ Role-based UI (admin / viewer)
▸ Live data via REST polling
▸ Runs in any modern browser
→
→

## Slide 4
Hardware Components
Three sensors covering all key OT environmental parameters
SCD30
Sensirion
CO₂ · Temperature · Humidity
I²C @ 0x61
CO₂ Range
400–10,000 ppm
Temp Range
-40 to +70 °C
Humidity
0–95 %RH
Interface
I²C (10 kHz)
Address
0x61 (fixed)
Power
3.3V / 19 mA
BME280
Bosch Sensortec
Barometric Pressure
I²C @ 0x76
Pressure Range
300–1100 hPa
Accuracy
±1 hPa
Temp Range
-40 to +85 °C
Interface
I²C (shared bus)
Address
0x76 (SDO→GND)
Power
3.3V / 3.6 µA
PMS5003
Plantower
PM1.0 · PM2.5 · PM10
UART2 @ 9600
PM Range
0–500 µg/m³
Resolution
1 µg/m³
Technology
Laser scattering
Interface
UART2 @ 9600
Port
/dev/ttyAMA1
Power
5V / 100 mA
Raspberry Pi 4 Model B
Host platform · 64-bit ARM Cortex-A72 · 2–8 GB RAM · Ubuntu/RPi OS Bookworm

## Slide 5
GPIO Wiring Diagram
All sensors connect to the 40-pin GPIO header — no soldering required
Raspberry Pi 4
Pin 1
3.3V
Pin 2
5V
Pin 3
GPIO2 / SDA1
Pin 5
GPIO3 / SCL1
Pin 6
GND
Pin 9
GND
Pin 11
GPIO17
Pin 13
GPIO27
Pin 21
GPIO9 / UART2 RX
Pin 24
GPIO8 / UART2 TX
Sensor Connections
SCD30
VCC → Pin 1 (3.3V)
SCD30
GND → Pin 6 (GND)
SCD30
SDA → Pin 3 (GPIO2 / SDA1)
SCD30
SCL → Pin 5 (GPIO3 / SCL1)
SCD30
SEL → Pin 6 (GND) ← I²C mode select
BME280
VCC → Pin 1 (3.3V)
BME280
GND → Pin 6 (GND)
BME280
SDA → Pin 3 (shared with SCD30)
BME280
SCL → Pin 5 (shared with SCD30)
BME280
SDO → Pin 6 (GND) ← addr = 0x76
PMS5003
VCC → Pin 2 (5V)
PMS5003
GND → Pin 9 (GND)
PMS5003
SET → Pin 11 (GPIO17 HIGH)
PMS5003
TX → Pin 21 (UART2 RX)
PMS5003
RX → Pin 24 (UART2 TX)

## Slide 6
Dashboard — Monitor Panel
Real-time KPI cards, trend charts, and particulate matter bars updated every 2 seconds
Live KPI Cards
Temperature, Humidity, PM1, PM2.5, PM10, CO₂, Battery, Power Source updated every 2 seconds
Battery Warning Banner
Auto-shown when battery < 30%. Covers the full width for immediate staff attention
Trend Chart
10-minute rolling temperature and humidity waveforms
PM Bar Chart
PM1 / PM2.5 / PM10 relative bars with real µg/m³ values

## Slide 7
Dashboard — Settings Panel
Admin-only threshold configuration and user management; viewer gets read-only access
Sensor Thresholds Table
Per-parameter Ideal / Best (L1) / Good (L2) thresholds editable by admin — saved to backend
Device Configuration
Set OT type (OT / ICU) and room name — used in CSV export filenames
User Management
Admin-only section: list users, add with role, delete — persisted to users.json between restarts
Role-Based UI
Save button hidden for viewers. User Management section completely hidden for non-admin sessions

## Slide 8
Dashboard — Alarms & History Panels
Alarm log and 24-hour telemetry history pulled live from the SQLite database
ALARM LOG
▸ Parameter name + timestamp + OT ID
▸ WARNING / ALARM level badge (colour)
▸ Sorted latest-first from SQLite
▸ Auto-refreshes on nav click
HISTORY TABLE
▸ Last 24 hours of telemetry rows
▸ Columns: Time / Temp / Humidity / PM2.5 / CO₂
▸ Pulls from GET /history?hours=24
▸ CSV export via DOWNLOAD button (auth required)

## Slide 9
Authentication & Role-Based Access
HMAC-SHA256 signed session cookies · Two roles: admin and viewer
1 LOGIN
User clicks AUTH button Enters username + password
2 VERIFY
POST /auth/login Backend checks users.json + config.yaml
3 SESSION COOKIE
HMAC-SHA256 token set as HttpOnly cookie (60 min expiry)
4 ROLE UI
Admin sees full controls Viewer sees read-only User Mgmt hidden
→
→
→
Role Capabilities
Capability
Admin 🔑
Viewer 👁
Monitor panel (live data)
✓
✓
Download CSV
✓
✓
View Alarms / History
✓
✓
Edit thresholds
✓
✗ (hidden)
Manage users
✓
✗ (hidden)
Acknowledge alarms
✓
✗

## Slide 10
Alarm Engine — Threshold Rules
NABH / ASHRAE 170 compliant thresholds with hysteresis to prevent alarm fatigue
Parameter Thresholds (ASHRAE 170 / WHO 2021)
Parameter
Nominal
Warning Low
Warning High
Alarm Low
Alarm High
Temperature (°C)
21
20
24
18
25
Humidity (%RH)
52
40
60
30
70
CO₂ (ppm)
—
—
1000
—
1200
PM2.5 (µg/m³)
5
—
12
—
25
PM10 (µg/m³)
10
—
20
—
50
Pressure (hPa)
1013
990
1030
970
1050
Hysteresis Design
Trigger Delay
Parameter must exceed threshold continuously for 5 seconds before an alarm fires
Clear Delay
Must stay back in safe range for 10 seconds before alarm clears (prevents chattering)
Combination Rule
PM2.5 spike + high occupancy together trigger elevated-risk notification
Alarm Levels
NORMAL → WARNING → ALARM → FAULT Each stored in SQLite alarm log

## Slide 11
Data Flow — End to End
From physical sensor to dashboard KPI card in under 2 seconds
SENSORS
SCD30 + BME280 + PMS5003 Read every 2 seconds via asyncio thread pool
HARDWARE SOURCE
HardwareSource assembles TelemetryPacket Timestamped in IST
ALARM ENGINE
Evaluate thresholds Apply hysteresis rules Fire callbacks on breach
STORAGE
Insert telemetry row Insert alarm event SQLite WAL mode
REST API
GET /history GET /alarms WebSocket broadcast
DASHBOARD
KPI cards update Alarm banners show History table fills
▶
▶
▶
▶
▶
Total end-to-end latency: < 2 seconds (poll interval = 2 s)
Storage & Retention
Database:
SQLite with WAL mode — concurrent reads without locking the write path
Telemetry:
1 row per 2-second poll · fields: ot_id, timestamp, temp, humidity, PM2.5, CO₂, pressure, status
Alarms:
Every threshold breach logged: parameter, level, value, message, acknowledged, duration
Retention:
90 days default (configurable) · auto-pruned every 6 hours by background task
Export:
GET /export/csv → downloadable audit report for NABH / infection control review

## Slide 12
Raspberry Pi Deployment
From fresh SD card to live dashboard in under 30 minutes
1
Flash SD Card
Raspberry Pi Imager → RPi OS Lite 64-bit Pre-configure SSH, hostname: ot-monitor
2
Enable Interfaces
/boot/firmware/config.txt: dtparam=i2c_arm_baudrate=10000 dtoverlay=uart2
3
Install Libraries
pip install adafruit-circuitpython-scd30 adafruit-circuitpython-bme280 pyserial
4
Test Sensors
python sensors/test_sensors.py All three sensors must show PASS before going to hardware mode
5
Configure & Run
config.yaml: data_source.type: hardware server.host: 0.0.0.0 Change session_secret + passwords
6
Autostart
systemd service: ot-monitor.service sudo systemctl enable ot-monitor Dashboard at :8001 on every boot
Access dashboard: http://ot-monitor.local:8001/ or http://<RPi-IP>:8001/

## Slide 13
Clinical & Regulatory Compliance
Thresholds derived from NABH, ASHRAE 170-2021, WHO IEQ 2021, ISO 14644-1
NABH
National Accreditation Board for Hospitals & Healthcare Providers (India) OT environment: 20–24°C, 40–60%RH, positive pressure ≥ 8 Pa, ≥ 20 Air Changes per Hour (ACH), HEPA filtration.
ASHRAE 170-2021
Ventilation of Health Care Facilities — North American standard adopted globally. OT: 20–24°C, 30–60%RH, ≥20 ACH total / ≥4 ACH outside air, PM2.5 ≤ 25 µg/m³, PM10 ≤ 50 µg/m³.
WHO IEQ 2021
Indoor Air Quality Guidelines (updated 2021). PM2.5 24-hr average ≤ 15 µg/m³, PM10 ≤ 45 µg/m³, CO₂ < 1000 ppm in occupied clinical spaces.
ISO 14644-1
Cleanrooms and Associated Controlled Environments. OT typically ISO Class 7 (Class 10,000): ≤ 352,000 particles ≥ 0.5µm per m³ — monitored via PMS5003.
All thresholds stored in config/config.yaml — editable via Settings panel (admin only) without restarting the backend

## Slide 14
SYSTEM SUMMARY
Complete Hardware Stack
Raspberry Pi 4 + SCD30 + BME280 + PMS5003 — all sensors integrated and tested
Real-Time Monitoring
6 environmental parameters polled every 2 seconds with live dashboard updates
Clinical Alarm Engine
NABH / ASHRAE 170 thresholds with hysteresis — zero false alarm fatigue
Secure Multi-User Access
HMAC-SHA256 sessions, role-based UI — admin vs viewer from any browser
90-Day Data Retention
SQLite time-series + alarm log, CSV export for audit and compliance reporting
Zero-Dependency Dashboard
Single HTML file served from backend — no build step, works on any device
http://ot-monitor.local:8001/
admin / OTAdmin2024 · nurse / OTNurse2024
OT Infection Monitoring System · Raspberry Pi 4 + SCD30 + BME280 + PMS5003 · June 2026